When you arrive:

- The fire department will probably have accessed the building by using their key box located at door C-3 and have activated the remote fire panel located in the C-3 entry.

- The panel will tell them which smoke detector, pull station, or other detector has activated.

- The fire panel was programed from the blueprints so the readout on the fire panel does not match the actual room numbers. Use the chart hanging on the remote panel to show or tell them where the device is that has gone off.

- If they determine it was a false alarm then they will reset the fire alarm panel.  If they do not know how to reset the panel see reset procedure on next page.

- After fire alarm is reset then they will need to reset the elevator. If they do not know how then see procedure on next page.

- Once the fire alarm and elevator are reset then press the security panel it should return to the normal screen. If it doesn’t press the “ACK’ button on the security panel and it should return to the normal screen.

- If a device has failed and the system will not reset then silence the fire alarm per procedure on next page and then press “ACK” button on security panel to silence it. Notify Chairman of Trustees that service on the system will be needed.

- If it was not a false alarm and there is damage to the building the fire department should begin clearing water and smoke from the building. Notify Chairman of Trustees and other Trustees so a plan of action can be determined.

RESETTING AFTER ALARM

- If the system alarmed and the fire department was called DO NOT reset the system until they tell you to do so.

- Determine why the system alarmed and reset that device. Open and close pull station with key or wait till smoke detector is blinking red and not steady red.

- Activate remote panel (if not already activated) by inserting key (on top of panel) into key slot and rotate a quarter turn to right.

- Main panel is always active simply open door and key should be in door. If not remote panel key is the same or use key number D-2 from the key box.

- Press the “____________” key on the screen.

- Then press the “System Reset” key and system should reset after a couple minutes.

- When screen comes up that says “System is normal” and has church logo remove key or close panel door.

- Press the “ACK” button on the security panel to return it to normal screens if it has not already done so.

SILENCING AFTER ALARM

- If fire department was called and it is a known false alarm the system may be silenced. However DO NOT reset the system till the fire department says to do so.

- Activate remote panel (if not already activated) by inserting key (on top of panel) into key slot and rotate a quarter turn to right.

- Main panel is always active simply open door and key should be in door. If not remote panel key is the same or use key number D-2 from the key box.

- Press the “____________” key on the screen.

- Then press the “System Silence” button and system will silence.

- Remove key or close panel door.

- Press the “ACK” button on the security panel to silence it.

SILENCING A TROUBLE ALARM

- Activate remote panel (if not already activated) by inserting key (on top of panel) into key slot and rotate a quarter turn to right.

- Main panel is always active simply open door and key should be in door. If not remote panel key is the same or use key number D-2 from the key box.

- Press the “AKC” button on the screen system will silence.

- Remove key or close panel door.

- Press the “ACK” button on the security panel to silence it.

SPRINKLER HEAD ACTIVATION

- If a sprinkler head is broken off or damaged a large volume of water will begin flowing into the building.

- The fire alarm will sound and the fire department will be called and respond.

- If we are certain the system was damaged and there is no fire we can shut the system down to minimize damage to the building.

- Go to the sprinkler riser located in the southwest corner of the gym.

- Close the “Main” valve.

- Open the “Drain “valve.

- Silence the fire alarm and wait for fire department.

- Notify Trustees and begin cleanup.